## June'15
Availability Calculation for the Period : From 01.06.2015 To 30.06.2015 (Powerlinks Lines)
a. Intra-regional element - ER
Sl. No. | Element Code | Element Name | Total Available Hours | Duration Of Outage Attributable to Powerlinks (OH) | Common | Attributable to Powergrid & others (exclude the outage system constraints) |  | Outage not to be taken into consideration |  | Total Duration Available for Consideration (THM) | NSC | Ckt. kMS. | OHxNSCxCkt kMs | THMxNSCxCkt kMs | Non Availability Factor/Month (NAFM) | Transmission System Availability Factor (TAFM) | Outage Percentage
outage
for
[5 empty] | PGCIL |  |  | NC | Grid Incident system constraints
PTL
A | B | C | D | E |  | F |  | G | H | I=D-G | J | K | L=ExJxK | M=IxJxK | N=L/M | O=100-100xNAFM | P=NAFM%
- | - | - | Hours | Hrs:Min |  | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Nos. | kms | - |  |  |  | -
Powerlinks Intra-Regional Lines
1 | PTL400ER01 | 400kV NSLG-NPRN-III | 720:00 | 5:24 |  | 5:09 | 0:00 | 0:00 | 0:56 | 720:00 | 4 | 160.082 | 144.0738 | 19209.84 | 0.0075 | 99.25% | 0.75%
2 | PTL400ER02 | 400kV NSLG-NPRN-IV | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 4 | 160.082 | 0 | 19209.84 | 0 | 100% | 0%
3 | PTL400ER03 | 400kV NPRN-MUZ-1 | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 4 | 238.531 | 0 | 28623.72 | 0 | 100% | 0%
4 | PTL400ER04 | 400kV NPRN-MUZ-II | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 4 | 238.531 | 0 | 28623.72 | 0 | 100% | 0%
5 | PTL220ER01 | MUZ-KANTI(BSEB)-I | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 3:56 | 720:00 | 1 | 24.05 | 0 | 721.5 | 0 | 100% | 0%
6 | PTL220ER02 | MUZ-KANTI(BSEB)-II | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 1 | 24.05 | 0 | 721.5 | 0 | 100% | 0%
|  |  |  | 5:24 |  | 5:09 | 0:00 | 0:00 | 4:52 | 4320:00 |  |  | 144.0738 | 97110.12 | 0.0014836 | 99.85% | 0.1484%
Availability of Intra-Regional Powerlinks Lines for the month of June' 2015:- | [6 empty] | 99.85%