## April'15
Availability Calculation for the Period : From 01.04.2015 To 30.04.2015 (Powerlinks Lines)
a. Intra-regional element - ER
Sl. No. | Element Code | Element Name | Total Available Hours | Duration Of Outage Attributable to Powerlinks (OH) | Common | Attributable to Powergrid & others (exclude the outage system constraints) |  | Outage not to be taken into consideration |  | Total Duration Available for Consideration (THM) | NSC | Ckt. kMS. | OHxNSCxCkt kMs | THMxNSCxCkt kMs | Non Availability Factor/Month (NAFM) | Transmission System Availability Factor (TAFM) | Outage Percentage
outage
for
[5 empty] | PGCIL |  |  | NC | Grid Incident system constraints
PTL
A | B | C | D | E |  | F |  | G | H | I=D-G | J | K | L=ExJxK | M=IxJxK | N=L/M | O=100-100xNAFM | P=NAFM%
- | - | - | Hours | Hrs:Min |  | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Nos. | kms | - |  |  |  | -
Powerlinks Intra-Regional Lines
1 | PTL400ER01 | 400kV NSLG-NPRN-III | 720:00 | 0:00 |  | 0:00 | 0:00 | 1:52 | 0:00 | 718:08 | 4 | 160.082 | 0 | 19160.0367 | 0 | 100% | 0%
2 | PTL400ER02 | 400kV NSLG-NPRN-IV | 720:00 | 15:29 |  | 0:00 | 0:00 | 0:00 | 0:52 | 720:00 | 4 | 160.082 | 413.1005 | 19209.84 | 0.021505 | 97.85% | 2.15%
3 | PTL400ER03 | 400kV NPRN-MUZ-1 | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 4 | 238.531 | 0 | 28623.72 | 0 | 100% | 0%
4 | PTL400ER04 | 400kV NPRN-MUZ-II | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 4 | 238.531 | 0 | 28623.72 | 0 | 100% | 0%
5 | PTL220ER01 | MUZ-KANTI(BSEB)-I | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 1 | 24.05 | 0 | 721.5 | 0 | 100% | 0%
6 | PTL220ER02 | MUZ-KANTI(BSEB)-II | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 1 | 24.05 | 0 | 721.5 | 0 | 100% | 0%
|  |  |  | 15:29 |  | 0:00 | 0:00 | 1:52 | 0:52 | 4318:08 |  |  | 413.1005 | 97060.3167 | 0.0042561 | 99.57% | 0.4256%
Availability of Intra-Regional Powerlinks Lines for the month of April' 2015:- | [6 empty] | 99.57%

## May'15
Availability Calculation for the Period : From 01.05.2015 To 31.05.2015 (Powerlinks Lines)
a. Intra-regional element - ER
Sl. No. | Element Code | Element Name | Total Available Hours | Duration Of Outage Attributable to Powerlinks (OH) | Common | Attributable to Powergrid & others (exclude the outage system constraints) |  | Outage not to be taken into consideration |  | Total Duration Available for Consideration (THM) | NSC | Ckt. kMS. | OHxNSCxCkt kMs | THMxNSCxCkt kMs | Non Availability Factor/Month (NAFM) | Transmission System Availability Factor (TAFM) | Outage Percentage
outage
for
[5 empty] | PGCIL |  |  | NC | Grid Incident system constraints
PTL
A | B | C | D | E |  | F |  | G | H | I=D-G | J | K | L=ExJxK | M=IxJxK | N=L/M | O=100-100xNAFM | P=NAFM%
- | - | - | Hours | Hrs:Min |  | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Nos. | kms | - |  |  |  | -
Powerlinks Intra-Regional Lines
1 | PTL400ER01 | 400kV NSLG-NPRN-III | 744:00 | 0:00 |  | 9:33 | 0:00 | 0:00 | 0:00 | 744:00 | 4 | 160.082 | 0 | 19850.168 | 0 | 100% | 0%
2 | PTL400ER02 | 400kV NSLG-NPRN-IV | 744:00 | 0:00 |  | 16:24 | 0:00 | 0:00 | 0:00 | 744:00 | 4 | 160.082 | 0 | 19850.168 | 0 | 100% | 0%
3 | PTL400ER03 | 400kV NPRN-MUZ-1 | 744:00 | 69:45 |  | 0:00 | 0:00 | 0:00 | 9:07 | 744:00 | 4 | 238.531 | 2772.9229 | 29577.844 | 0.09375 | 90.62% | 9.375%
4 | PTL400ER04 | 400kV NPRN-MUZ-II | 744:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 744:00 | 4 | 238.531 | 0 | 29577.844 | 0 | 100% | 0%
5 | PTL220ER01 | MUZ-KANTI(BSEB)-I | 744:00 | 0:00 |  | 0:00 | 9:41 | 0:00 | 0:00 | 744:00 | 1 | 24.05 | 0 | 745.55 | 0 | 100% | 0%
6 | PTL220ER02 | MUZ-KANTI(BSEB)-II | 744:00 | 0:00 |  | 0:00 | 16:56 | 0:00 | 0:00 | 744:00 | 1 | 24.05 | 0 | 745.55 | 0 | 100% | 0%
|  |  |  | 69:45 |  | 25:57 | 26:37 | 0:00 | 9:07 | 4464:00 |  |  | 2772.9229 | 100347.124 | 0.027633 | 97.24% | 2.763%
Availability of Intra-Regional Powerlinks Lines for the month of May' 2015:- | [6 empty] | 97.24%