## Pvsnl PTL Aug'18
| Aug | Availability Calculation for the month of August 18 for Powerlink Lines in ER | [13 empty] | 2018
| Element Name | Attributable to PL |  | Attributable to Others |  | Act of God/Grid Incident |  | Outage Under the Category of Deemed available |  | Total Outage |  | Ti | TNAi | Wi (SIL*Ckt Km) | Wi(Ti-TNAi)/Ti | 100*Wi(Ti-TNAi)/(Ti*Wi)
|  | Hrs | Mins | Hrs | Mins | Hrs | Mins | Hrs | Min | Hrs | Min | Hrs | Hrs
| 400 KV NSLG-KSNE-I | 0 | 0 | 9 | 9 | 0 | 0 | 0 | 0 |  |  | 734.85 | 0 | 64088.856 | 64088.856 | 100
| 400 KV NSLG-KSNE- II | 0 | 0 | 8 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 735.0833 | 0 | 64088.856 | 64088.856 | 100
| 400 KV KSNE-NPRN-I | 0 | 0 | 9 | 42 | 0 | 0 | 0 | 0 |  |  | 734.3 | 0 | 45343.374 | 45343.374 | 100
| 400 KV KSNE-NPRN-II | 0 | 0 | 10 | 41 | 0 | 0 | 0 | 0 | 10 | 41 | 733.3167 | 0 | 45343.374 | 45343.374 | 100
| 400 KV NPRN-MUZ-I | 0 | 0 | 6 | 5 | 0 | 0 | 0 | 0 | 6 | 5 | 737.9167 | 0 | 125705.837 | 125705.837 | 100
| 400 KV NPRN-MUZ-II | 0 | 0 | 4 | 24 | 0 | 0 | 0 | 0 | 4 | 24 | 739.6 | 0 | 125705.837 | 125705.837 | 100
| 220 KV MUZ-KANTI-I | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 3174.6 | 3174.6 | 100
| 220 KV MUZ-KANTI-II | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 3174.6 | 3174.6 | 100
|  | 0 | 0 | 46 | 176 | 0 | 0 | 0 | 0 | 20 | 70 | 5903.0667 |  | 476625.334 | 476625.334 | 800
| Availability | 1
% | Availability | 100

## Sheet1
AVAILABILITY INDEX FOR AUGUST -2018
a. Intra-regional element - ER
S.NO. | ELEMENT NAME | ELEMENT WISE AVAILABILITY ACHIEVED | TARGET AVAILABILITY AS PER SOP
TRANSMISSION LINES
1 | 400 KV NSLG-KSNE-I | 100% | 90%
2 | 400 KV NSLG-KSNE- II | 100% | 90%
3 | 400 KV KSNE-NPRN-I | 100% | 90%
4 | 400 KV KSNE-NPRN-II | 100% | 90%
5 | 400 KV NPRN-MUZ-I | 100% | 90%
6 | 400 KV NPRN-MUZ-II | 100% | 90%
7 | 220 KV MUZ-KANTI-I | 100% | 90%
8 | 220 KV MUZ-KANTI-II | 100% | 90%