## April'16
Availability Calculation for the Period : From 01.04.2016 To 30.04.2016 (Powerlinks Lines)
a. Intra-regional element - ER
Sl. No. | Element Code | Element Name | Total Available Hours | Duration Of Outage Attributable to Powerlinks (OH) | Common | Attributable to Powergrid & others (exclude the outage system constraints) |  | Outage not to be taken into consideration |  | Total Duration Available for Consideration (THM) | NSC | Ckt. kMS. | OHxNSCxCkt kMs | THMxNSCxCkt kMs | Non Availability Factor/Month (NAFM) | Transmission System Availability Factor (TAFM) | Outage Percentage
outage
for
[5 empty] | PGCIL |  |  | NC | Grid Incident system constraints
PTL
A | B | C | D | E |  | F |  | G | H | I=D-G | J | K | L=ExJxK | M=IxJxK | N=L/M | O=100-100xNAFM | P=NAFM%
- | - | - | Hours | Hrs:Min |  | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Nos. | kms | - |  |  |  | -
Powerlinks Intra-Regional Lines
1 | PTL400ER01 | 400kV NSLG-NPRN-III | 720:00 | 5:44 |  | 0:00 | 0:53 | 0:00 | 1:36 | 720:00 | 4 | 160.082 | 152.9672 | 19209.84 | 0.007963 | 99.2% | 0.7963%
2 | PTL400ER02 | 400kV NSLG-NPRN-IV | 720:00 | 0:00 |  | 0:00 | 0:55 | 0:00 | 0:00 | 720:00 | 4 | 160.082 | 0 | 19209.84 | 0 | 100% | 0%
3 | PTL400ER03 | 400kV NPRN-MUZ-1 | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 4 | 238.531 | 0 | 28623.72 | 0 | 100% | 0%
4 | PTL400ER04 | 400kV NPRN-MUZ-II | 720:00 | 55:22 |  | 4:40 | 0:00 | 0:00 | 6:43 | 720:00 | 4 | 238.531 | 2201.1111 | 28623.72 | 0.076898 | 92.31% | 7.69%
5 | PTL220ER01 | MUZ-KANTI(BSEB)-I | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:28 | 720:00 | 1 | 24.05 | 0 | 721.5 | 0 | 100% | 0%
6 | PTL220ER02 | MUZ-KANTI(BSEB)-II | 720:00 | 0:00 |  | 0:00 | 2:52 | 0:00 | 0:32 | 720:00 | 1 | 24.05 | 0 | 721.5 | 0 | 100% | 0%
|  |  |  | 61:06 |  | 4:40 | 4:40 | 0:00 | 9:19 | 4320:00 |  |  | 2354.0783 | 97110.12 | 0.024241 | 97.58% | 2.424%
Availability of Intra-Regional Powerlinks Lines for the month of April' 2016:- | [6 empty] | 97.58%

## May'2016
Availability Calculation for the Period : From 01.05.2016 To 31.05.2016 (Powerlinks Lines)
a. Intra-regional element - ER
Sl. No. | Element Code | Element Name | Total Available Hours | Duration Of Outage Attributable to Powerlinks (OH) | Common | Attributable to Powergrid & others (exclude the outage system constraints) |  | Outage not to be taken into consideration |  | Total Duration Available for Consideration (THM) | NSC | Ckt. kMS. | OHxNSCxCkt kMs | THMxNSCxCkt kMs | Non Availability Factor/Month (NAFM) | Transmission System Availability Factor (TAFM) | Outage Percentage
outage
for
[5 empty] | PGCIL |  |  | NC | Grid Incident system constraints
PTL
A | B | C | D | E |  | F |  | G | H | I=D-G | J | K | L=ExJxK | M=IxJxK | N=L/M | O=100-100xNAFM | P=NAFM%
- | - | - | Hours | Hrs:Min |  | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Nos. | kms | - |  |  |  | -
Powerlinks Intra-Regional Lines
1 | PTL400ER01 | 400kV NSLG-NPRN-III | 744:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 744:00 | 4 | 160.082 | 0 | 19850.168 | 0 | 100% | 0%
2 | PTL400ER02 | 400kV NSLG-NPRN-IV | 744:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 744:00 | 4 | 160.082 | 0 | 19850.168 | 0 | 100% | 0%
3 | PTL400ER03 | 400kV NPRN-MUZ-1 | 744:00 | 0:00 |  | 0:00 | 0:00 | 11:01 | 0:00 | 732:59 | 4 | 238.531 | 0 | 29139.8746 | 0 | 100% | 0%
4 | PTL400ER04 | 400kV NPRN-MUZ-II | 744:00 | 40:16 |  | 0:00 | 0:00 | 0:00 | 3:09 | 744:00 | 4 | 238.531 | 1600.808 | 29577.844 | 0.054122 | 94.59% | 5.412%
5 | PTL220ER01 | MUZ-KANTI(BSEB)-I | 744:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 744:00 | 1 | 24.05 | 0 | 745.55 | 0 | 100% | 0%
6 | PTL220ER02 | MUZ-KANTI(BSEB)-II | 744:00 | 0:00 |  | 0:00 | 1:31 | 0:00 | 0:00 | 744:00 | 1 | 24.05 | 0 | 745.55 | 0 | 100% | 0%
|  |  |  | 40:16 |  | 0:00 | 1:31 | 11:01 | 3:09 | 4452:59 |  |  | 1600.808 | 99909.1546 | 0.016023 | 98.4% | 1.602%
Availability of Intra-Regional Powerlinks Lines for the month of May' 2016:- | [6 empty] | 98.4%

## Feb'17_PTL
Availability Calculation for the Period : From 01.02.2017 To 28.02.2017 (Powerlinks Lines)
a. Intra-regional element - ER
Sl. No. | Element Code | Element Name | Total Available Hours | Duration Of Outage Attributable to Powerlinks (OH) | Common | Attributable to Powergrid & others (exclude the outage system constraints) |  | Outage not to be taken into consideration |  | Total Duration Available for Consideration (THM) | NSC | Ckt. kMS. | OHxNSCxCkt kMs | THMxNSCxCkt kMs | Non Availability Factor/Month (NAFM) | Transmission System Availability Factor (TAFM) | Outage Percentage
outage
for
[5 empty] | PGCIL |  |  | NC | Grid Incident system constraints
PTL
A | B | C | D | E |  | F |  | G | H | I=D-G | J | K | L=ExJxK | M=IxJxK | N=L/M | O=100-100xNAFM | P=NAFM%
- | - | - | Hours | Hrs:Min |  | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Nos. | kms | - |  |  |  | -
Powerlinks Intra-Regional Lines
1 | PTL400ER01_1 | 400kV NSLG-KISHANGANJ-I | 672:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 672:00 | 4 | 93.188 | 0 | 10437.056 | 0 | 100% | 0%
2 | PTL400ER02_1 | 400kV NSLG-KISHANGANJ-II | 672:00 | 15:07 |  | 0:00 | 0:00 | 0:00 | 1:25 | 672:00 | 4 | 93.188 | 234.782 | 10437.056 | 0.022495 | 97.75% | 2.25%
1 | PTL400ER01_2 | 400kV NPRN-KISHANGANJ-I | 672:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 672:00 | 4 | 66.002 | 0 | 7392.224 | 0 | 100% | 0%
2 | PTL400ER02_2 | 400kV NPRN-KISHANGANJ-II | 672:00 | 49:47 |  | 0:00 | 0:00 | 0:00 | 0:38 | 672:00 | 4 | 66.002 | 547.6333 | 7392.224 | 0.074082 | 92.59% | 7.408%
3 | PTL400ER03 | 400kV NPRN-MUZ-1 | 672:00 | 2:18 |  | 0:00 | 0:00 | 0:00 | 0:00 | 672:00 | 4 | 238.531 | 91.4369 | 26715.472 | 0.0034226 | 99.66% | 0.3423%
4 | PTL400ER04 | 400kV NPRN-MUZ-II | 672:00 | 5:44 |  | 0:00 | 0:00 | 0:00 | 0:54 | 672:00 | 4 | 238.531 | 227.9296 | 26715.472 | 0.0085317 | 99.15% | 0.8532%
5 | PTL220ER01 | MUZ-KANTI(BSEB)-I | 672:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 672:00 | 1 | 24.05 | 0 | 673.4 | 0 | 100% | 0%
6 | PTL220ER02 | MUZ-KANTI(BSEB)-II | 672:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 672:00 | 1 | 24.05 | 0 | 673.4 | 0 | 100% | 0%
|  |  |  | 72:56 |  | 0:00 | 0:00 | 0:00 | 2:57 | 5376:00 |  |  | 1101.7818 | 90436.304 | 0.012183 | 98.78% | 1.218%
Availability of Intra-Regional Powerlinks Lines for the month of February' 2017:- | [6 empty] | 98.78%

## Sheet1
AVAILABILITY INDEX FOR Feb -2017
a. Intra-regional element - ER
S.NO. | VOLTAGE LEVEL | ELEMENT NAME | ELEMENT WISE AVAILABILITY ACHIEVED | TARGET AVAILABILITY AS PER SOP
TRANSMISSION LINES
1 | PTL400ER01 | 400kV NSLG-NPRN-III | 100% | 90%
2 | PTL400ER02 | 400kV NSLG-NPRN-IV | 97.75% | 90%
3 | PTL400ER03 | 400kV NPRN-MUZ-1 | 100% | 90%
4 | PTL400ER04 | 400kV NPRN-MUZ-II | 92.59% | 90%
5 | PTL220ER01 | MUZ-KANTI(BSEB)-I | 99.66% | 90%
6 | PTL220ER02 | MUZ-KANTI(BSEB)-II | 99.15% | 90%