## Jan'17_PTL
Availability Calculation for the Period : From 01.01.2017 To 31.01.2017 (Powerlinks Lines)
a. Intra-regional element - ER
Sl. No. | Element Code | Element Name | Total Available Hours | Duration Of Outage Attributable to Powerlinks (OH) | Common | Attributable to Powergrid & others (exclude the outage system constraints) |  | Outage not to be taken into consideration |  | Total Duration Available for Consideration (THM) | NSC | Ckt. kMS. | OHxNSCxCkt kMs | THMxNSCxCkt kMs | Non Availability Factor/Month (NAFM) | Transmission System Availability Factor (TAFM) | Outage Percentage
outage
for
[5 empty] | PGCIL |  |  | NC | Grid Incident system constraints
PTL
A | B | C | D | E |  | F |  | G | H | I=D-G | J | K | L=ExJxK | M=IxJxK | N=L/M | O=100-100xNAFM | P=NAFM%
- | - | - | Hours | Hrs:Min |  | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Nos. | kms | - |  |  |  | -
Powerlinks Intra-Regional Lines
1 | PTL400ER01_1 | 400kV NSLG-KISHANGANJ-I | 744:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 744:00 | 4 | 93.188 | 0 | 11555.312 | 0 | 100% | 0%
2 | PTL400ER02_1 | 400kV NSLG-KISHANGANJ-II | 744:00 | 21:31 |  | 0:00 | 0:00 | 0:00 | 1:37 | 744:00 | 4 | 93.188 | 334.1825 | 11555.312 | 0.02892 | 97.11% | 2.892%
1 | PTL400ER01_2 | 400kV NPRN-KISHANGANJ-I | 744:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 744:00 | 4 | 66.002 | 0 | 8184.248 | 0 | 100% | 0%
2 | PTL400ER02_2 | 400kV NPRN-KISHANGANJ-II | 744:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 744:00 | 4 | 66.002 | 0 | 8184.248 | 0 | 100% | 0%
3 | PTL400ER03 | 400kV NPRN-MUZ-1 | 744:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 744:00 | 4 | 238.531 | 0 | 29577.844 | 0 | 100% | 0%
4 | PTL400ER04 | 400kV NPRN-MUZ-II | 744:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 744:00 | 4 | 238.531 | 0 | 29577.844 | 0 | 100% | 0%
5 | PTL220ER01 | MUZ-KANTI(BSEB)-I | 744:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 744:00 | 1 | 24.05 | 0 | 745.55 | 0 | 100% | 0%
6 | PTL220ER02 | MUZ-KANTI(BSEB)-II | 744:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 744:00 | 1 | 24.05 | 0 | 745.55 | 0 | 100% | 0%
|  |  |  | 21:31 |  | 0:00 | 0:00 | 0:00 | 1:37 | 5952:00 |  |  | 334.1825 | 100125.908 | 0.0033376 | 99.67% | 0.3338%
Availability of Intra-Regional Powerlinks Lines for the month of Jan' 2017:- | [6 empty] | 99.67%

## Sheet1
AVAILABILITY INDEX FOR Jan -2017
a. Intra-regional element - ER
S.NO. | VOLTAGE LEVEL | ELEMENT NAME | ELEMENT WISE AVAILABILITY ACHIEVED | TARGET AVAILABILITY AS PER SOP
TRANSMISSION LINES
1 | PTL400ER01 | 400kV NSLG-NPRN-III | 100% | 90%
2 | PTL400ER02 | 400kV NSLG-NPRN-IV | 97.11% | 90%
3 | PTL400ER03 | 400kV NPRN-MUZ-1 | 100% | 90%
4 | PTL400ER04 | 400kV NPRN-MUZ-II | 100% | 90%
5 | PTL220ER01 | MUZ-KANTI(BSEB)-I | 100% | 90%
6 | PTL220ER02 | MUZ-KANTI(BSEB)-II | 100% | 90%