## Nov'16_PTL
Availability Calculation for the Period : From 01.11.2016 To 30.11.2016 (Powerlinks Lines)
a. Intra-regional element - ER
Sl. No. | Element Code | Element Name | Total Available Hours | Duration Of Outage Attributable to Powerlinks (OH) | Common | Attributable to Powergrid & others (exclude the outage system constraints) |  | Outage not to be taken into consideration |  | Total Duration Available for Consideration (THM) | NSC | Ckt. kMS. | OHxNSCxCkt kMs | THMxNSCxCkt kMs | Non Availability Factor/Month (NAFM) | Transmission System Availability Factor (TAFM) | Outage Percentage
outage
for
[5 empty] | PGCIL |  |  | NC | Grid Incident system constraints
PTL
A | B | C | D | E |  | F |  | G | H | I=D-G | J | K | L=ExJxK | M=IxJxK | N=L/M | O=100-100xNAFM | P=NAFM%
- | - | - | Hours | Hrs:Min |  | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Nos. | kms | - |  |  |  | -
Powerlinks Intra-Regional Lines
1 | PTL400ER01_1 | 400kV NSLG-KISHANGANJ-I | 720:00 | 56:36 |  | 0:00 | 0:00 | 0:00 | 5:55 | 720:00 | 4 | 93.188 | 879.0735 | 11182.56 | 0.078611 | 92.14% | 7.861%
2 | PTL400ER02_1 | 400kV NSLG-KISHANGANJ-II | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 4 | 93.188 | 0 | 11182.56 | 0 | 100% | 0%
1 | PTL400ER01_2 | 400kV NPRN-KISHANGANJ-I | 720:00 | 62:22 |  | 0:00 | 0:00 | 0:00 | 2:25 | 720:00 | 4 | 66.002 | 686.0541 | 7920.24 | 0.08662 | 91.34% | 8.662%
2 | PTL400ER02_2 | 400kV NPRN-KISHANGANJ-II | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 4 | 66.002 | 0 | 7920.24 | 0 | 100% | 0%
3 | PTL400ER03 | 400kV NPRN-MUZ-1 | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 4 | 238.531 | 0 | 28623.72 | 0 | 100% | 0%
4 | PTL400ER04 | 400kV NPRN-MUZ-II | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 4 | 238.531 | 0 | 28623.72 | 0 | 100% | 0%
5 | PTL220ER01 | MUZ-KANTI(BSEB)-I | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 1 | 24.05 | 0 | 721.5 | 0 | 100% | 0%
6 | PTL220ER02 | MUZ-KANTI(BSEB)-II | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 1 | 24.05 | 0 | 721.5 | 0 | 100% | 0%
|  |  |  | 118:58 |  | 0:00 | 0:00 | 0:00 | 8:20 | 5760:00 |  |  | 1565.1276 | 96896.04 | 0.016153 | 98.38% | 1.615%
Availability of Intra-Regional Powerlinks Lines for the month of Nov' 2016:- | [6 empty] | 98.38%

## Sheet1
AVAILABILITY INDEX FOR NOV -2016
a. Intra-regional element - ER
S.NO. | VOLTAGE LEVEL | ELEMENT NAME | ELEMENT WISE AVAILABILITY ACHIEVED | TARGET AVAILABILITY AS PER SOP
TRANSMISSION LINES
1 | PTL400ER01 | 400kV NSLG-NPRN-III | 92.14% | 90%
2 | PTL400ER02 | 400kV NSLG-NPRN-IV | 100% | 90%
3 | PTL400ER03 | 400kV NPRN-MUZ-1 | 91.34% | 90%
4 | PTL400ER04 | 400kV NPRN-MUZ-II | 100% | 90%
5 | PTL220ER01 | MUZ-KANTI(BSEB)-I | 100% | 90%
6 | PTL220ER02 | MUZ-KANTI(BSEB)-II | 100% | 90%