## NRPC monthly format
Provisional Availability Calculation for the Period : From 01.11.2016 To 30.11.2016 (Powerlinks' Lines)
a. Intra-regional element - NR
Sl. No. | Element Code | Element Name | Total Available Hours | Duration Of Outage Attributable to Powerlinks (OH) | Common | Attributable to Powergrid & others (exclude the outage system constraints) |  | Outage not to be taken into consideration |  |  | Total Duration Available for Consideration (THM) | NSC | Ckt. km | OHxNSCxCkt kMs | THMxNSCxCkt kMs | Non Availability Factor/Month (NAFM) | Transmission System Availability Factor (TAFM) | Outage Percentage
outage
for
[5 empty] | PGCIL |  |  | NC | Grid Incident /System constraints | Deemed Available
PTL
A | B | C | D | E |  | F |  | G | H | -- | I=D-G-H | J | K | L=ExJxK | M=IxJxK | N=L/M | O=100-100xNAFM | P=NAFM%
- | - | - | Hours | Hrs:Min |  | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Nos. | kms | - |  |  |  | -
Powerlinks Intra-Regional Lines
1 | PTL400NR15 | 400kV BLY(PGCIL)-MRT(PGCIL)-I | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 2 | 183.322 | 0 | 10999.32 | 0 | 100% | 0%
2 | PTL400NR13 | 400kV BLY(PGCIL)-MRT(PGCIL)-II | 720:00 | 3:40 |  | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 2 | 183.322 | 56.0151 | 10999.32 | 0.0050926 | 99.49% | 0.5093%
3 | PTL400NR16 | 400kV MRT(PGCIL)-MND(PGCIL)-III | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 2 | 47.509 | 0 | 2850.54 | 0 | 100% | 0%
3 | PTL400NR14 | 400kV MRT(PGCIL)-MND(PGCIL)-IV | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 2 | 47.509 | 0 | 2850.54 | 0 | 100% | 0%
4 | PTL400NR09 | 400kV BLY(UPPCL)-BLY(PGCIL)-I | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 2 | 5.126 | 0 | 307.56 | 0 | 100% | 0%
5 | PTL400NR10 | 400kV BLY(UPPCL)-BLY(PGCIL)-II | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 2 | 5.126 | 0 | 307.56 | 0 | 100% | 0%
6 | PTL400NR07 | 400kV GKP-LKO-I | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 2 | 245.905 | 0 | 14754.3 | 0 | 100% | 0%
7 | PTL400NR08 | 400kV GKP-LKO-II | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 720:00 | 2 | 245.905 | 0 | 14754.3 | 0 | 100% | 0%
|  |  |  | 3:40 |  | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 5760:00 |  |  | 56.0151 | 57823.44 | 0.00096873 | 99.9% | 0.09687%
|  | Availability of Intra-Regional Powerlinks Lines |  |  |  |  | 99.9%
b. Inter-regional element (ER - NR)
Sl. No. | Element Code | Element Name | Total Available Hours | Duration Of Outage Attributable to Powerlinks (OH) | Common | Attributable to Powergrid & others (exclude the outage system constraints) |  | Outage not to be taken into consideration |  |  | Total Duration Available for Consideration (THM) | NSC | Ckt. kMS. | OHxNSCxCkt kMs | THMxNSCxCkt kMs | Non Availability Factor/Month (NAFM) | Transmission System Availability Factor (TAFM) | Outage Percentage
outage
for
[5 empty] | PGCIL |  |  | NC | Grid Incident /System constraints | Deemed Available
PTL
A | B | C | D | E |  | F |  | G | H | -- | I=D-G-H | J | K | L=ExJxK | M=IxJxK | N=L/M | O=100-100xNAFM | P=NAFM%
- | - | - | Hours | Hrs:Min |  | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Nos. | kms | - |  |  |  | -
Powerlinks Inter-Regional Lines
1 | PTL400IR05 | 400kV GKP-MZP-1 | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 00:00:00 | 720:00 | 4 | 260.399 | 0 | 31247.88 | 0 | 100% | 0%
2 | PTL400IR06 | 400kV GKP-MZP-2 | 720:00 | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 00:00:00 | 720:00 | 4 | 260.399 | 0 | 31247.88 | 0 | 100% | 0%
|  |  |  | 0:00 |  | 0:00 | 0:00 | 0:00 | 0:00 | 00:00:00 | 1440:00 |  |  | 0 | 62495.76 | 0 | 100% | 0%
|  | Availability of Inter-Regional Powerlinks Lines |  |  |  |  | 100%

## Sheet1
AVAILABILITY INDEX FOR NOVEMBER -2016
a. Intra-regional element - NR
S.NO. | VOLTAGE LEVEL | ELEMENT NAME | ELEMENT WISE AVAILABILITY ACHIEVED | TARGET AVAILABILITY AS PER SOP
TRANSMISSION LINES
1 | PTL400NR15 | 400kV BLY(PGCIL)-MRT(PGCIL)-I | 100% | 90%
2 | PTL400NR13 | 400kV BLY(PGCIL)-MRT(PGCIL)-II | 99.49% | 90%
3 | PTL400NR16 | 400kV MRT(PGCIL)-MND(PGCIL)-III | 100% | 90%
3 | PTL400NR14 | 400kV MRT(PGCIL)-MND(PGCIL)-IV | 100% | 90%
4 | PTL400NR09 | 400kV BLY(UPPCL)-BLY(PGCIL)-I | 100% | 90%
5 | PTL400NR10 | 400kV BLY(UPPCL)-BLY(PGCIL)-II | 100% | 90%
6 | PTL400NR07 | 400kV GKP-LKO-I | 100% | 90%
7 | PTL400NR08 | 400kV GKP-LKO-II | 100% | 90%
b. Inter-regional element (ER - NR)
S.NO. | VOLTAGE LEVEL | ELEMENT NAME | ELEMENT WISE AVAILABILITY ACHIEVED | TARGET AVAILABILITY AS PER SOP
TRANSMISSION LINES
1 | PTL400IR05 | 400kV GKP-MZP-1 | 100% | 90%
2 | PTL400IR06 | 400kV GKP-MZP-2 | 100% | 90%